# [Enter project title]

Design building information modelling execution plan template

HIQ-PLN-00004

# Copyright

[enter project title] – Design building information modelling (BIM) execution plan

Published by the State of Queensland (Queensland Health), June 2026

This document is licensed under a Creative Commons Attribution 3.0 Australia licence. To view a copy of this licence, visit creativecommons.org/licenses/by/3.0/au

© State of Queensland (Queensland Health) 2026

You are free to copy, communicate and adapt the work, as long as you attribute the State of Queensland (Queensland Health).

For more information contact:
Health Infrastructure Queensland, Department of Health, GPO Box 48, Brisbane QLD 4001, email hiqdesigninnovationandassurance@health.qld.gov.au, phone (07) 3328 9310.

An electronic version of this document is available at https://www.health.qld.gov.au/system-governance/health-infrastructure/resources/building-information-modelling or via the Queensland Health Design Collaboration site.

Disclaimer

The content presented in this publication is distributed by the Queensland Government as an information source only. The State of Queensland makes no statements, representations or warranties about the accuracy, completeness or reliability of any information contained in this publication. The State of Queensland disclaims all responsibility and all liability (including without limitation for liability in negligence) for all expenses, losses, damages and costs you might incur as a result of the information being inaccurate or incomplete in any way, and for any reason reliance was placed on such information.

Project summary

Please provide some general information of the project.

| HHS | [refer to PIR Section 4.1] |
| --- | --- |
| Facility name | [refer to PIR Section 4.1] |
| Project address/location | [refer to PIR Section 4.1] |

Document control

Please add the document author and organisation below .

| Prepared by | [refer to PIR Section 4.1– BIM manager] |
| --- | --- |
| Title | [refer to PIR Section 4.1– BIM manager] |
| Company | [refer to PIR Section 4.1– BIM manager] |
| Contact details | [refer to PIR Section 4.1– BIM manager] |

Version history

Please track versions of the document below, including draft releases, minor and major updates.

All changes, also during project delivery must be tracked below.

| #### Version no. | #### Date | #### Changed by | #### Nature of amendment |
| --- | --- | --- | --- |
| 0.1 |  |  | Initial draft |
| 0.2 |  |  | minor revision |
| 1.0 |  |  | major revision |

Contents

Copyright	1

Terms	5

Acronyms	8

1 Purpose of this document	9

1.1 Document structure	10

2 Introduction	11

3 Overview	13

3.1 Building information modelling execution  plan overview	13

3.2 dRofus management plan overview	13

3.3 Project summary/description	13

3.4 Reference documents and shared resources	13

4 Commercial	15

4.1 Procurement strategy	15

4.2 Project schedule	15

4.3 Amendments to project information requirements	15

4.4 Non-required uses of building information modelling–delivery team uses	16

4.5 Delivery team	17

5 Management	18

5.1 Project location and set-out	18

5.2 Building information modelling coordination meetings	19

5.3 User group and stakeholder communication processes	19

5.4 Existing conditions modelling	20

5.5 Functional design brief	20

5.6 Masterplan	20

5.7 Schematic design	22

5.8 Detailed design	25

5.9 Tender documentation	30

5.10 Construction documentation	32

5.11 Construction	39

6 Technical	40

6.1 Software selection	40

6.2 Project common data environment	41

6.3 Industry foundation classes	42

6.4 Information requirements	43

6.5 Documentation	45

6.6 Schedules	45

6.7 Room data sheets	45

6.8 Federated model and coordination	45

6.9 Quality assurance and control	46

7 Appendices	47

7.1 Appendix A – Building information modelling manager	47

7.2 Appendix B – Quantity surveyor requirements or model content plan	47

# Terms

| #### Term | #### Definition |
| --- | --- |
| Alphanumerical information | Structured Information expressed using characters, digits and symbols or tokens. May be attached or linked to geometry. Further described in ISO 7817-1:2024. |
| Appointed party | A provider of information for the project, including services and typically has a lead party such as an architect or managing contractor. |
| Asset Information Model (AIM) | Information model relating to the operational stage: as per AS ISO 19650. |
| Asset Information Requirements (AIR) | Information requirements in relation to the operation of the asset: as per AS ISO 19650. |
| BIM Execution Plan (BEP) | A detailed plan, created from the Queensland Health BEP template, that documents the use of BIM on a project. It outlines who is responsible for what in the BIM process, when in the process they are responsible for it, and how they will execute Queensland Health requirements as specified in the Project Information Requirements (PIR) and Capital Infrastructure Requirements (CIR). |
| BEP template | The standard Queensland Health Building Information Modelling (BIM) execution plan template is to be used by delivery teams. Refers to Design BEP (DBEP) and Construction BEP (CBEP). |
| Building Information Modelling (BIM) | The use of a shared digital representation of a built asset to facilitate design, construction and operation processes to form a reliable basis for decisions. |
| Building Information Models (BIM/s) | Means all models that any contributing party (or its sub-contractors) is required to produce and deliver in accordance with the BEP, PIR and CIR. |
| BIM manager | A delivery team provided resource to manage the BIM and asset information creation processes on the project. |
| Capital works | The planning, design, construction and delivery of new assets or significant upgrades to existing infrastructure, typically funded through a capital investment program. In the context of Queensland Health, capital works include healthcare facilities and associated infrastructure delivered to meet service needs. |
| Common Data Environment (CDE) | Cloud-based collaboration software to host design files, with an integration into BIM authoring software and other software. |
| Delivery team | A collection of appointed parties contributing to the capital works project—the composition of which may change according to the project requirements and schedule, but typically comprises design consultants, contractor and sub-contractors, as per AS ISO 19650. For the purposes of this document, the delivery team excludes Queensland Health and its internal project managers as its representatives. |
| Exchange Information Requirements (EIR) | Queensland Health requirements to enable the exchange of information from the PIM to the AIM. In this instance, the EIR is combined with the PIR to reduce the number of documents to be reviewed by the delivery team. |
| Federated model | An assembly of discipline/trade BIM/s combined for uses such as coordination, collaboration, and exchange with the appointing party. |
| Geometrical information | Structured Information, such as geometry-based CAD or BIM models. Further described in ISO 7817-1:2024. |
| Key decision | A business decision that Queensland Health values, which can be made using information created by the delivery team. |
| Level of Development (LOD) | The degree to which the element’s geometry and attached information have been progressed, and the degree to which delivery team members may rely on the information when using the model. Queensland Health doesn’t specify the LOD requirements per stage; however, if the delivery team wishes to use an LOD framework, the 2024 LOD specification published by the US BIMForum shall be used as a guiding reference. |
| Level of information | The specific data associated with the individual objects within the BIM. |
| Level of information need | The ‘Level of information need’ provides methods for describing information to be exchanged according to the EIR and namely the PIR, as per AS ISO 7817.1:2024. |
| Laser scanning | The process of capturing digital information about the shape of an object with equipment that uses a laser to measure the distance between itself and the object, resulting in a point cloud. |
| Massing model | An early volumetric model useful for understanding bulk and scale, areas of floor plates and departmental layouts and adjacencies. |
| Model Content Plan (MCP) | A Quantity Surveyor (QS) developed document that defines the modelling requirements (units of measure, codification) for the delivery team to enable the QS to perform cost estimating from BIM. |
| Model element | An individual component within a BIM (e.g. wall, floor, nurse call device, room, diffuser, column, etc.). |
| Model element author | A person responsible for creating an element (object) in the BIM environment. |
| openBIM | A universal approach to the collaborative design, realisation and operation of buildings based on open standards and workflows. |
| Photogrammetry | The process of extracting 3D information from photos or video to convert into digital models or point clouds. |
| Project brief | Queensland Health requirements for a specific project. |
| Project Information Model (PIM) | The information model relating to the delivery stage. The PIM consists of documentation, alphanumerical information and geometrical information of the project, typically using BIM, CAD and GIS. As per AS ISO 19650. |
| Project Information Requirements (PIR) | Queensland Health information requirements and exchange processes to enable the creation and management of the PIM to support the ongoing AIM (this document). |
| Project manager | A Queensland Health assigned resource to ensure the delivery team complies with the PIR and BEP, enabling the creation of the PIM and AIM. The Project manager's responsibility is to manage the scope, time, cost, quality, resources, communications, and risk aspects of the project. |
| Space planning platform | Queensland Health use dRofus as their space planning tool, integrated with BIM. dRofus is used with a HIQ template for clinical planning, FF+E management, and asset data consolidation and quality control, amongst other functions. |

# Acronyms

| #### Abbreviated terms | #### Definition |
| --- | --- |
| 3D | Three-dimensional digital model |
| AusHFG | Australasian Health Facility Guidelines |
| AIM | Asset Information Model |
| AIR | Asset Information Requirements |
| BIM | Building Information Modelling |
| BIM/s | Building Information Models |
| BEP | BIM Execution Plan (refers to DBEP and CBEP) |
| CAD | Computer Aided Design/Drafting |
| CDE | Common Data Environment |
| CBEP | Construction BIM Execution Plan |
| CIR | Capital Infrastructure Requirements |
| CMMS | Computer Maintenance Management System |
| DBEP | Design BIM Execution Plan |
| FF+E | Furniture Fixture and Equipment |
| GUID | Global Unique Identifier |
| HHS | Hospital and Health Service |
| HIQ | Health Infrastructure Division |
| IFC | Industry Foundation Classes |
| LOD | Level of Development |
| LOI | Level of Information |
| PIM | Project Information Model |
| PIR | Project Information Requirements |
| PSM | Permanent Survey Marker |
| RDS | Room Data Sheets |
| SiD | Safety in Design |
| SoA | Schedule of Accommodation |

- 1 Purpose of this document

Using the Queensland Health Project Information Requirements (PIR), this design Building Information Modelling (BIM) Execution Plan (DBEP) template is to be populated in Microsoft Word by the tendering delivery team for the named project.

Track changes must be used to highlight any changes between the original document and all subsequent revisions. Once agreed by the delivery team and Queensland Health, accept changes and record a summary in the version history table on page three.

The DBEP outlines the delivery team’s proposed approach to using BIM/s and information management practices for the design stages that the delivery team are engaged to perform. Before the start of a new major stage (schematic design, detailed design, construction documentation, etc.), the DBEP shall be reviewed, revised and agreed with the Queensland Health project management, confirming the approach for that stage.

The design BIM/s will be utilised by other appointed parties, including the Quantity Surveyor (QS) for costing purposes and the contractor for informing the tender and construction process. Ultimately, the production of as-built BIM/s containing asset data for the project will be handed over to the Hospital and Health Service (HHS).

The delivery team is to use any of the following information sources to assist in the creation of this document, please reach out to the HIQ project director if you haven’t received those documents:

- Queensland Health Capital Infrastructure Requirements (CIR).

- Queensland Health PIR for BIM.

- Queensland Health asset equipment lists.

- Queensland Health BIM data uploader template.

- Queensland Health dRofus management plan.

- Any existing conditions HHS BIM/s.

- Existing 2D drawings, reports and schedules.

- Survey information, including laser scans.

- HHS critical information requirements (e.g. naming, coding, classifications).

- Functional design brief and any space planning information.

- AusHFG codes and guidelines.

The DBEP must be developed by the proposed BIM manager, taking into consideration the needs of the delivery team and Queensland Health PIR and CIR. The DBEP will be used as part of the assessment criteria for determining a preferred delivery team for design stages.

The DBEP will always be created prior to the development of the Construction BEP (CBEP). The DBEP and federated model will be used by tendering contractors to inform the development of the CBEP and construction BIM/s.

1.1 Document structure

The document is divided into commercial, managerial and technical sections in alignment with ISO 19650. The managerial section is further split into the logical project delivery stages. In this way, appointed parties can work through the project delivery stages, understanding the specific BIM requirements for each discipline for the given stage.

This document articulates how information shall be structured, managed and delivered by the delivery team contracted by Queensland Health, in alignment with the PIR.

As changes during project delivery are inevitable, such as new delivery team members joining the project, the BEP shall be revised by the BIM manager when any new appointed party joins the project and/or before each new project stage commences.

Instructional text (hidden blue text) for the lead appointed party Instructional text is provided to assist the lead appointed party’s BIM manager in developing this document using Microsoft Word. If you do not see any blue text below, then enable visibility in: File > Options > Display > check Hidden Text (blue text should be visible below). Note: Hidden text should be turned off prior to publishing the document and placeholder text [in square brackets] must be deleted. DELETE THIS INSTRUCTIONAL NOTE BEFORE FINALISING THIS DBEP

DOCUMENT USE—instructional text is shown in this way.

PIR section reference

DO NOT DELETE instructional text as it contains the section references to the project information requirements which will aid you in completing this document. Hide instructional text prior to issue to Queensland Health. To hide it, go to File > Options > Display > Hidden Text and uncheck the box. The final BEP may be issued to the wider delivery team as a PDF.

Text in [square brackets]

All text in [square brackets] should be replaced with the delivery team approaches.

2 Introduction

| Queensland Health BIM objectives |  |  |  |
| --- | --- | --- | --- |
| #### No | #### BIM objective | #### Required uses of BIM by appointed parties | #### BIM tiers |
| 1 | BIM is procured and incorporated into project delivery (PIR 2.1) | From the earliest outset, a BIM Execution Plan (BEP) is to be created, based on PIR and CIR. The BEP is administered and updated by the delivery team BIM manager. | ALL |
| 2 | Improving collaboration, coordination and capacity (PIR 2.2) | Discipline/trade BIM/s are to be combined into a federated model and used for collaboration, and as a primary decision-making tool for coordination. | ALL |
| 3 | Platform agnostic—use of openBIM formats (PIR 2.3) | Both native formats and Industry Foundation Classes (IFC) are contractual deliverables at handover. | ALL |
| 4 | Structured and gradual development of BIM to provide an as-built dataset (PIR 2.4) | Continual development of the planning and design BIM/s to support the construction/as-built BIM/s, and any associated information requirements. | ALL |
| 5 | Improved data structuring and Information coordination (PIR 2.5) | Schedule of Accommodation (SoA), drawings, schedules, Australasian Health Facilities Guidelines (AusHFG) + HHS asset coding to be coordinated and linked to BIM. | ALL |
| 6 | Benefits realisation is measured and tracked (PIR 2.6) | BIM benefits realisations is discussed and reported at milestone deliverables by the delivery team using the Queensland Health BIM metrics for projects.xlsx. | ALL |
| 7 | Clearer design + construction comprehension (PIR 2.7) | The delivery team shall leverage BIM visualisation tools (3D collaboration tools that may be supplemented with VR/AR) to help inform stakeholders of design/constructability solutions. | ALL |
| 8 | Enhanced space planning (PIR 2.8) | The space planning platform (dRofus) shall be integrated with the BIM/s and used to manage functional briefing, validate SoA, room, FF+E, and asset data. | Tier 1 + 2 only |
| 9 | Workplace Health and Safety (WHS) in BIM (PIR 2.9) | Identified Safety in Design (SiD) risks must be navigable within the federated model to improve understanding and minimise or eliminate these risks. | Tier 1 + 2 only |
| 10 | Quantity surveying from BIM (PIR 2.10) | The Quantity Surveyor (QS) or cost estimator is to use design BIM/s to inform the cost planning activities, including whole-of-life costs. | Tier 1 + 2 only |
| 11 | BIM to be used for operational planning and staging (PIR 2.11) | The delivery team is to leverage BIM for operational planning, decanting and staging, and construction planning. | Tier 1 only |

Table 1: BIM requirements related to project scale

3 Overview

## 3.1 Building information modelling execution 
plan overview

PIR section 2 (d and f) and 4.1. Appointed parties to nominate the BIM manager and collaboratively develop the BEP.

- Refer to the Queensland Health PIR for details of:

  - responsibilities of the delivery team and BIM manager

  - purpose of the DBEP and CBEP

  - production, development and implementation of the DBEP and CBEP

  - updating the DBEP and CBEP prior to the commencement of a new project stage or when a material change affects the contents of this document as per Section 4.1 of the PIR.

## 3.2 dRofus management plan overview

PIR Section 2 (e) and 3.2. Appointed parties to nominate the dRofus lead who must then develop and continue to update the dRofus Management Plan.

This document must be read in conjunction with the dRofus management plan.

## 3.3 Project summary/description

PIR section 4.1 (a). Design BIM manager to insert a brief description of the project here.

[enter project description here]

## 3.4 Reference documents and shared resources

Design BIM manager—the first table indicates the version of the TEMPLATE documents, and the second table indicates the current version of the documents used on this project, to allow for future comparison.

The current revision of the Queensland Health capital delivery documents is recorded below.

| Document | Version | Date |
| --- | --- | --- |
| CIR | [enter version] | [DD/MM/YYYY] |
| Queensland Health PIR | [enter version] | [DD/MM/YYYY] |
| DBEP template |  |  |
| CBEP template |  |  |
| dRofus management plan template |  |  |
| Queensland Health asset equipment lists |  |  |
| Queensland Health BIM data uploader template |  |  |
| Classification (Uniclass) |  |  |
| NABERS emission factors database |  |  |
| NABERS Environmental Product Declarations (EPD) codes |  |  |

Table 2: Reference documents

| Document | Version | Date |
| --- | --- | --- |
| DBEP | [enter version] | [DD/MM/YYYY] |
| CBEP |  |  |
| dRofus management plan |  |  |
| Model content plan |  |  |

Table 3: Project documents

4 Commercial

4.1 Procurement strategy

The BIM manager is responsible for documenting the procurement strategy. Examples of procurement methods include:

- Managing contractor

- Design and Construct (D+C)

- Early Contractor Involvement (ECI)

- Public-Private Partnership (PPP)

If unknown, write ‘to be confirmed’. If the procurement strategy involves the designer as part of the contractor engagement, the DBEP and CBEP can be combined into one document, the Design and Construction BEP, using the Queensland Health templates.

[Enter procurement method here]

4.2 Project schedule

PIR section 4.1 (b). The BIM manager is to complete table 4.

The estimated dates for major project milestones, as they relate to Queensland Health project stages, are shown in table 4.

| #### Project stage or milestone | #### Estimated start date | #### Estimated completion date |
| --- | --- | --- |
| Functional design brief | [DD/MM/YYYY] | [DD/MM/YYYY] |
| Masterplan | [DD/MM/YYYY] | [DD/MM/YYYY] |
| Schematic design | [DD/MM/YYYY] | [DD/MM/YYYY] |
| Detailed design | [DD/MM/YYYY] | [DD/MM/YYYY] |
| Tender documentation | [DD/MM/YYYY] | [DD/MM/YYYY] |
| Construction documentation | [DD/MM/YYYY] | [DD/MM/YYYY] |
| Construction | [TBC or as per CBEP – Rev] | [TBC or as per CBEP – Rev] |
| Commissioning/handover | [TBC or as per CBEP – Rev] | [TBC or as per CBEP – Rev] |
| Project evaluation | [TBC or as per CBEP – Rev] | [TBC or as per CBEP – Rev] |

Table 4: Project schedule

4.3 Amendments to project information requirements

PIR section 2 (g). Appointed parties to document any issues, technical or capability/capacity challenges, then seek Queensland Health project manager approval.

The following amendments to the Queensland Health PIR are proposed for this project.

| #### PIR Clause No. | #### Clause title | #### Amendment |
| --- | --- | --- |
| [enter clause] | [enter title] | [enter change] |

Table 5: PIR concerns

## 4.4 Non-required uses of building information modelling–delivery team uses

PIR section 4.1 (e). Any non-Queensland Health required BIM uses or processes that the delivery team feel are necessary to complete the design and construction of the project (beyond those stated in the PIR) must be detailed below. This is to clearly differentiate these uses independently to the requirements of Queensland Health. Appointed parties must document any BIM use not available to Queensland Health i.e. delivery team uses only.

The following table identifies the uses of BIM not specified by Queensland Health.

| #### Stage | #### Use | #### By whom | #### Comments |
| --- | --- | --- | --- |
| Masterplanning |  |  |  |
| Schematic design | [e.g. Computational design algorithms] | [Architect] | [Computational design analysis models will be used to inform the architectural BIM but will not be provided to Queensland Health] |
| Detailed design | [e.g. Structural engineering analysis] | [Structural engineer] | [The structural analysis model will be used to inform the structural BIM but will not be provided to Queensland Health] |
| Construction documentation |  |  |  |

Table 6: Delivery team uses of BIM (not required by Queensland Health)

| #### Role | #### Discipline | #### Name | #### Company | #### Email/phone |
| --- | --- | --- | --- | --- |
| Quantity surveyor | Cost planning |  |  |  |
| BIM manager | BIM |  |  |  |
| dRofus lead | Space planning |  |  |  |
| Civil engineer | Civil |  |  |  |
| Architectural BIM lead | Architecture |  |  |  |
| Structural BIM lead | Structure |  |  |  |
| Mechanical BIM lead | Mechanical |  |  |  |
| Hydraulic BIM lead | Hydraulic |  |  |  |
| Electrical BIM lead | Electrical |  |  |  |
| Vertical transportation BIM lead | Vertical transportation |  |  |  |

4.5 Delivery team

PIR section 4.1 (g). The BIM manager is to complete the table below and add other disciplines/trades as necessary. If this table is completed pre-tender, write ‘TBA’ against the unknown consultants. Add extra delivery team members as necessary when known and include their BIM approaches in all updates to the DBEP, for Queensland Health approval.

List the QS, including whether this role sits with the client, contractor, or a novated design consultant. Where not yet known, write ‘TBA’.

The contact details for key stakeholders involved in planning and managing BIM on this project are detailed in table 7.

Table 7: Key project team members

- 5 Management

The following sections detail the collaboration and communication procedures for local and remote users to access and use BIM for decision-making. The delivery team BIM manager is responsible for ensuring all deliverables listed in this section are successfully produced.

5.1 Project location and set-out

PIR section 4.5 states that the BIM manager must nominate a master coordinates file and record the project coordinates in the table below.

Master coordinates file name: [enter master coordinates file name here]

| #### Attribute | #### Details |
| --- | --- |
| Geodetic datum | [enter the horizontal datum used for survey control (must be GDA2020)] |
| Projection/CRS | [enter the projected coordinate system and EPSG code (e.g. MGA Zone 56, EPSG:7856)] |
| Height datum | [enter the vertical datum used for elevation (e.g. AHD71)] |
| Permanent Survey Marker (PSM) (or equivalent known survey point) | [enter the name and coordinates of the known site survey point] Name: N/S (Y): E/W (X): Elevation (Z): |
| Project base point (e.g. local grid intersection) | [enter the location of the project base point coordinates] Location: N/S (Y): E/W (X): Elevation (Z): |
| Project location description | [enter the project’s general location using cardinal directions from a known place] |
| Model rotation | [enter the angle in degrees, clockwise from true north to project north] |
| Coordinate units (m or mm) | [enter the units of the coordinate values] |

Table 8: Model geographic location

5.2 Building information modelling coordination meetings

PIR Section 4.3

The following table specifies the BIM meetings, timings, and location.

| #### Meeting | #### Timings | #### Location |
| --- | --- | --- |
| BIM execution planning | 2 weeks after contract awards | [populate] |
| Safety in design workshop | [enter as per project delivery schedule] | [populate] |
| 3D coordination/clash resolution | Fortnightly | [populate] |
| 3D design review meetings | Fortnightly | [populate] |
| Information requirements planning (with HHS) | Commencement of every project stage | [populate] |

Table 9: Meetings

5.3 User group and stakeholder communication processes

PIR Section 4.1 (h) and 2.7.

The user group and stakeholder communication processes (including the use of the BIM for staging, decanting and operational planning) are documented below.

[enter stakeholder strategy here]

Building information modelling requirements by project stages

5.4 Existing conditions modelling

PIR Section 3.3: Appointed parties to document any previous HHS existing conditions information (2D drawings), new survey and the extents of existing conditions to be modelled.

[enter extent of existing conditions modelling here]

## 5.5 Functional design brief

PIR Section 3.4. During the functional design brief stage, the creation of a BIM is optional; however, collaboration with HHS facility managers and other delivery team members to document the BEP approaches (including the critical information requirements) shall be undertaken to finalise the BEP, prior to master planning. The use of dRofus for the project shall be defined at this stage (if tier one or two) and developed before any modelling in BIM occurs. The approaches shall be documented below.

The BIM/s and space planning data are not required for submission to Queensland Health at functional design brief but may be used by the delivery team to document any initial concept designs.

dRofus must be set up before any modelling takes place for tier one or tier two projects.

[enter additional delivery team items here]

5.5.1 Functional design brief building information modelling deliverables

- Critical HHS information requirements to be documented in section 6.4 of the DBEP.

- Proposed BIM manager allocated.

- The DBEP shall be defined for at least master plan deliverables (i.e. the next project stage).

- Proposed project-specific BIM benefits realisation metrics for design, documented in Queensland Health BIM metrics for projects.xlsx template.

5.6 Masterplan

PIR Section 3.5. During the master plan stage, the creation of a BIM masterplan massing model shall be achieved through a BIM-enabled platform, enabling continuity from the master plan to schematic design. A site BIM and a preliminary existing condition BIM shall be initiated in this stage, with the approach documented below.

### 5.6.1 Overview

BIM/s created prior to the master plan must contain the requirements of the functional design brief above, as well as the following:

  - A site BIM created, with the current survey included and site benchmark, the project set out point and nominal building grids and levels/stories identified.

  - A preliminary existing conditions BIM/s created (based on Section 5.4) and existing elements identifiable as existing via an attribute (extents of the existing conditions model to be defined and agreed with the HHS facility manager and documented in DBEP).

  - Existing subsurface services must meet the quality requirements of AS 5488: Classification of subsurface utility information for quality level classification.

  - Masterplan massing models are to be accurately geo-located from the site BIM (as managed by the BIM manager) to ensure correct coordination between disciplines for all BIM/s.

  - Levels/storeys and grids to be managed by the BIM manager and coordinated across disciplines.

  - Population of dRofus with the project briefed SoA must be achieved prior to the commencement of schematic design and bi-directional synchronisation must occur before submission in accordance with the dRofus management plan.

[enter additional delivery team items here].

### 5.6.2 Masterplan building information modelling deliverables

- Documented and agreed DBEP for the stages the delivery team are engaged for, including the proposed approach to the information containers (SoA, RDS, cost plan, etc.) and BIM/s (architectural, structural, civil, hydraulic, fire, electrical, etc.) in a diagram for inclusion in the BEP.

- Proposed massing model/BIM (inclusive of design areas and analysis) for the preferred option, in native formats (if multiple models are being used, please share as transmittal package, e.g. eTransmit).

- 3D visualisations, general arrangement drawings, departmental functional diagrams.

- Tier one and two projects—defined approach to SiD and WHS risk management and how these will be displayed in BIM.

- Tier one and two projects—model content plan developed by the QS as per Appendix B.

- Tier and two projects—dRofus management plan developed and environment setup.

- Tier one projects—high-level operational staging diagrams shall be produced from the masterplan massing model.

- Benefits realisation metrics documented in the Queensland Health BIM metrics for projects.xlsx template, agreed between appointed parties and Queensland.

5.7 Schematic design

PIR Section 3.6. During the schematic design stage, the creation of all relevant discipline BIM/s is required to allow for collaboration and documentation of the schematic design. The proposed delivery team approach to BIM must be documented below.

### 5.7.1 Overview

BIM/s created prior to schematic design must contain the requirements of the master plan stage above, as well as the following:

- The design and documentation across all design disciplines, unless otherwise agreed and documented in this DBEP, must use a BIM authoring tool capable of producing the required output data (IFC 4 or later) and documentation as specified for all project deliverables.

- The use of BIM by all delivery teams is mandatory and shall form part of the stakeholder engagement and communication process. Typically, at this stage, model elements shall represent discrete systems, objects or assemblies that are individually identifiable and selectable at the component level. The use of grouped or repurposed foundational elements (e.g. walls, slabs, beams) to represent distinct modelled components is not permitted. Alphanumeric information shall also be attached to the model elements.

- All BIM/s must be correctly geospatially referenced, and a federated model created.

- The federated model, built from IFC format trade/discipline BIM/s, delivered in the agreed format (as agreed per project), exchanged fortnightly during the schematic design stage, is used for coordination and accessible to Queensland Health.

- All parameters in Queensland Health BIM Shared Parameters.txt shall be added to BIM/s from the provided Queensland Health Project Schedules (Revit)_2024.rvt if authoring tools permit or use the attributes by grouping tab in the Queensland Health asset equipment list spreadsheet.

- The appointed BIM manager is to undertake high-level geometrical and alphanumerical coordination activities (i.e. all BIM/s correctly georeferenced, correct attributes/parameters created). Coordination reports are not required until the detailed design stage.

- The BIM/s are to include spatial data defining designed net square metres, net volume and hold data to develop the room finish schedule/s, including room name, number and department.

- Model elements must be integrated and synchronised with the spatial planning or database tool, including the architectural, mechanical, electrical, hydraulic and fire protection services BIM/s. BIM/s are to include programme information to verify the designed space against the programmed/briefed space. Integration and synchronisation may also be required for other models as determined by this DBEP.

- Information requirements and the Queensland Health BIM shared parameters relevant to schematic design shall be populated in the BIM/s as per Section 4.14 of the PIR by each model element author as required.

- All schedules and Room Data Sheets (RDS) are to be produced from the data in dRofus.

- Virtual reality (VR) and Augmented reality (AR) must be used to engage with stakeholders/ user groups and gain final sign-off. Panorama renderings of key rooms shall be created, including simple ‘white card’ renderings.

- Model elements shall contain item coding (e.g. AusHFG) for rooms and all clinical FF+E, be aligned to the HHS information requirements and have the corresponding budget group as per HIQ ‘standardised FF+E groupings framework’ (e.g. 1, 2, or 3) attributes embedded.

- [Enter additional delivery team items here]

### 5.7.2 Architectural building information modelling

All other elements not mentioned below that the delivery team identifies as being required to complete deliverables for this stage must be agreed and a documented approach specified in the DBEP section below.

- Architectural BIM/s geospatially referenced to a site BIM/s, delivered in both native and IFC formats, with the following elements:

- Agreed extents of existing conditions modelled (Section 5.4) and all model elements to have an existing versus new attribute applied.

- Building extents (walls) are generically modelled, level to level.

- Nominal floor extents and thickness based on input from the structural engineer.

- Nominal roof extents and thickness to enclose the building based on input from the structural engineer.

- Indicative structural column locations based on input from the structural engineer.

- Generically modelled interior walls.

- Fenestration, windows, doors and openings modelled.

- Overhangs, sun shading modelled.

- Ceiling grid and fixture layout methodology discussed and agreed.

- Circulation areas (footpaths, walkways, ramps, stairs, vertical transportation, etc.) shall be generically modelled.

- Building, level, zones, room, departmental and critical asset naming nomenclature agreed with HHS, compliant with information requirements (PIR Section 4.14) and applied to BIM.

- Gross floor area, travel distances and engineering, gross departmental area (functional area plus circulation) for each functional unit, functional area for each functional unit and room, ready for reporting design area versus planned area.

- Integration and synchronisation of the BIM/s with dRofus.

- Tier one and two projects—defined approach to SiD and WHS risks linked to BIM.

- Tier one and two projects—SoA linked to BIM and cost plan through the use of a common classification schema.

- Tier one projects—high level: operational staging diagrams.

- [enter additional delivery team items here].

### 5.7.3 Quantity surveyor

All other elements not mentioned below that the delivery team identifies as being required to complete deliverables for this stage must be agreed and a documented approach specified in the DBEP section below.

A cost plan will be developed based on the following:

- The design intent BIM/s and dRofus project database created to date.

- The QS will take into consideration the modelled elements nominated above for each discipline.

- The QS will use the model content plan to ensure each discipline has created its discipline-specific BIM based on the required modelled elements for this stage.

- Any elements found by the QS, as per the requirements below, must be remedied immediately by the relevant model element author:

  - not modelled as per above and model content plan

  - incorrectly modelled (e.g. floors as stairs)

  - incorrectly categorised (e.g. ceilings as floors/slabs)

  - [enter additional delivery team items here].

### 5.7.4 Schematic design information requirements deliverables

Refer to Section 6.4 for details of the information requirements due at schematic design.

### 5.7.5 Schematic design building information modelling deliverables

The delivery team must produce BIM/s to a level that articulates the design intent and accurately represents the design solution by the end of schematic design, incorporating all of the elements in 5.7, including:

Documented and Queensland Health agreed DBEP for the stages the delivery team are engaged for.

- The delivery team must produce discipline-centric BIM/s in both native and IFC formats that define the design intent and accurately represent the schematic design solution. The BIM/s must incorporate all modelled elements nominated in this section.

- A federated model built from IFC format trade/discipline BIM/s, delivered in the agreed format (as agreed per project) at the required frequency.

- BIM/s and dRofus project database synchronised prior to extracts and delivery (if multiple models are being used, please share as transmittal package, e.g. eTransmit).

- All IFC BIM/s to contain Queensland Health asset parameters specific to the stage, mapped to their respective QH_Information property sets.

- Extract asset data from BIM and/or dRfous into the Queensland Health BIM data uploader template.xlsx template to check all BIM/s have been set up correctly

- Project stage-specific BIM benefits realisation metrics shall be documented in Queensland Health BIM metrics for projects.xlsx template

5.8 Detailed design

PIR Section 3.7. During the detailed design stage, creating all discipline BIM/s is necessary to facilitate collaboration, documentation and meet information requirements. The proposed delivery team approach to BIM must be documented below.

### 5.8.1 Overview

For detailed design onwards, the BIM/s must contain the requirements of the previous project stages above and incorporate the following:

- All Queensland Health parameters (refer to Queensland Health project schedules (Revit)_2024 or Queensland Health BIM shared parameters) must be added to BIM/s if not previously done.

- An integrated modelling process and coordination of modelled elements between all disciplines is required and must be documented in this DBEP.

- Virtual coordination and clash detection process for civil, architecture, structure and services are required. This process, including the process, documentation and reporting of detection and resolution outcomes, is clearly articulated in section 6.8 of the DBEP and reported to the Queensland Health project management at nominated intervals.

- Where existing buildings and/or structures are within the modelling boundary, traditional 2D documentation may be acceptable for some elements by agreement with Queensland Health and documented in Section 5.4.

- Where a design will interface with an existing building or structure, a laser scan survey of the existing building or structure, to which new elements may interface, may be procured as directed by Queensland Health. If procured, the laser scan survey must be used for coordination and made available to all consultants in a format that integrates with the model authoring software being used on the project.

- All general arrangement drawings, elevations and sections are to be generated from coordinated BIM/s to a scale of 1:50 and above. All smaller scales (i.e. 1:20, 1:10, 1:5, 1:2) are to be derived from the BIM/s and supplemented with 2D detail unless otherwise agreed by a Queensland Health representative and nominated in the DBEP.

- Supplementary 2D linework on the drawings may be required by the scale, in order to facilitate successful model coordination, quantity and cost extraction. For those details and enlarged sections agreed by the Queensland Health representative, not to be derived from the BIM/s, model element authors are to ensure that the geometry and data depicting the details and enlarged sections are coordinated with model elements. Details with significantly drafted content, such as 'standard' and 'typical' details, are not to contradict the model elements and shall utilise the BIM as an underlay when possible, for the purposes of verification and coordination.

- Any 2D drawings not derived from the BIM/s must be documented in the DBEP in Section 6.5.

- All instances of model elements in a service run must be allocated to a defined system.

- QH_ Asset parameters relevant to detailed design shall be populated in the BIM/s as per Section 4.14 of the PIR by each model element author as required.

- [enter additional delivery team items here].

### 8.8.2 Civil engineering building information modelling

All other elements not mentioned below that the delivery team identifies as being required to complete deliverables for this stage must be agreed and a documented approach specified in the DBEP section below.

- Existing topography.

- Proposed topography.

- Bulk excavation.

- Retaining walls.

- Carparks and roads.

- Major site services.

- Site drainage and overland flow paths.

- [enter additional delivery team items here].

### 5.8.3 Landscape architecture building information modelling

All other elements not mentioned below that the delivery team identifies as being required to complete deliverables for this stage must be agreed and a documented approach specified in this DBEP section below.

- Topography: 3D terrain of all site work as designed, including retaining walls. This model should include the site and surrounding areas that contribute to the site’s drainage system or otherwise impact the site. In most cases, this will require that adjacent roadways be modelled or linked from the civil model.

- Landscaping elements: planting areas, such as raised planting beds and berms, parking islands, pools/ponds/other water features, furniture, such as benches, bike racks and rubbish bins, terraces, fencing, gates and other items not included elsewhere in the federated model.

- Paving, grades, footpaths, curbs, gutters, site amenities and other elements typically included on enlarged scale site drawings in the vicinity of building/facility.

- [enter additional delivery team items here].

### 5.8.4 Architectural building information modelling

All other elements not mentioned below that the delivery team identifies as being required to complete deliverables for this stage must be agreed and a documented approach specified in this DBEP section below.

The architectural BIM/s requirements for schematic design must be incorporated, with the addition of the following:

- Architectural site requirements defined (refer also to civil engineering and landscape architecture).

- Internal and external architectural 3D imagery is required for project user group consultation and stakeholder consultation. The description of how this will be achieved (static visualisations, augmented and/or virtual reality) is to be clearly articulated in Section 5.2 of this DBEP.

- Room/spaces shall be defined, including accurate net square metres and net volume, based on geometry in the BIM/s with the level numbers, room names and numbers stored as a value within the space object and synchronised with dRofus.

- All finishes shall be coded with the wall type regardless of the thickness of the finish.

- Ceilings (with grids) and soffits shall be modelled at correct heights with annotations reporting the ceiling height above the finished floor level incorporated.

- Stairs, railings and ramps shall be modelled, railing details may be documented in 2D.

- All doors and windows and their respective openings shall be modelled to approximate size. The specific finish or material selection for these items must be included.

- Mechanical, electrical and hydraulic items that have architectural space requirements are to be placed in approximate locations in the correct rooms as generalised systems. The architect is to collaborate with the services engineers to determine the ownership of services and augment this BEP/model content plan as necessary. There is no requirement for a specific finish or material selection for these items.

- All budget group one, two and three and sub-group FF+E must be modelled with the appropriate value assigned to the element/object. The FF+E shall be depicted with correct overall shapes, sizes and installation heights, AusHFG code and placed in the briefed space. For tier one and two projects, refer to the dRofus Management Plan for a detailed list of FFE items required to be modelled.

- Clearance/maintenance zones for access, door swings, service space requirements and other operational clearances must be modelled and associated with the architectural modelled elements and checked for conflicts with other elements. These clearance zones should be easily identified as clearance zones and be associated with the equipment.

- [enter additional delivery team items here].

### 5.8.5 Structural building information modelling

All other elements not mentioned below that the delivery team identifies as being required to complete deliverables for this stage must be agreed and a documented approach specified in this DBEP section below.

- All foundations modelled, including piles with indicative depths, pads and footing elements with height, width, depth, top of foundation and concrete grade.

- Floors modelled including supports, construction and expansion joints and with penetrations 300mm diameter or greater.

- All necessary shafts, pits, sumps and openings modelled.

- Concrete framing, including beams and columns, modelled with the correct size and shape.

- Load-bearing walls, including openings, modelled.

- Primary and secondary steel framing, including truss, girts, beams, columns, joists and purlins modelled with correct sizes, shapes and lengths.

- Discrete elements must be modelled as per their construction (e.g. precast walls modelled as individual panels).

- Modelling ownership of all concrete stairs and landings and necessary openings, and steel stair framing members for stair systems shall be agreed with the architect and the relevant model element author and documented in the BEP/model content plan.

- Modelling ownership of the roof system shall be agreed with the architect and the relevant model element author documented in the BEP/model content plan.

- [enter additional delivery team items here].

### 5.8.6 Mechanical building information modelling

All other elements not mentioned below that the delivery team identifies as being required to complete deliverables for this stage must be agreed and a documented approach specified in this DBEP section below.

- Bound spaces and zones created with space names must match architectural room names and numbers.

- Equipment located and modelled as generalised systems, including fans, variable air volume systems compressors, chillers, cooling towers, air handlers, pumps and any other uniquely identifiable equipment.

- Duct main runs and branches for supply, return, ventilation and exhaust located with approximate sizes.

- Main pipes run at and over 50mm diameter (including insulation), modelled as generalised systems and place holders with indicative routes shown.

- Insulation around ductwork and pipework shall be shown, with insulation thickness included on the modelled ductwork and pipework. Insulation shall be separately indicated as a semi-transparent thickness around the duct and pipework.

- Diffusers, grilles, louvres, perimeter units and wall units are located as generalised systems.

- Clearance/maintenance zones for access, door swings, service space requirements, gauge reading, and other operational clearances must be modelled and associated with the mechanical services equipment and checked for conflicts with other elements. These clearance zones should be easily identified as clearance zones associated with the equipment.

- [enter additional delivery team items here].

### 5.8.7 Hydraulic building information modelling

All other elements not mentioned below that the delivery team identifies as being required to complete deliverables for this stage must be agreed and a documented approach specified in this DBEP section below.

- Stormwater, waste and vent as generalised systems.

- Piping modelled to room extents as generalised systems and/or to the fixture as agreed in the BEP/model content plan.

- Lagging/insulation around pipework shall be shown, with insulation thickness included on the modelled pipework. Insulation shall be separately indicated as a semi-transparent thickness around the pipework.

- Roof and floor drains, sumps, grease interceptors, tanks, water treatments and other major items.

- Supply water systems as generalised systems.

- Pumps.

- Modelling of fixtures to be agreed with the architect and documented in the BEP/model content plan (e.g. sinks, basins, toilet and bathroom fixtures, cisterns and water tanks).

- Clearance zones for access, service space requirements, gauge reading, valve clearances and other operational clearances must be modelled and associated with the plumbing system and checked for conflicts with other elements. These clearance zones should be modelled as transparent solids within the object.

- [enter additional delivery team items here]

### 5.8.8 Electrical building information modelling

All other elements not mentioned below that the delivery team identifies as being required to complete deliverables for this stage must be agreed and a documented approach specified in this DBEP section below.

- Power and telecommunications outlets, switches and junction boxes modelled.

- Interior and exterior transformers, emergency generators, and other equipment.

- Main and distribution panels and switchgear, including access clearances.

- Main intermediate distribution frames.

- Lighting fixtures, controls, switches and junction boxes modelled as generalised systems.

- Main and distribution panels modelled as generalised systems.

- Cable trays located.

- Conduits over 90mm diameter modelled.

- Clearance zones for access, door swings, service space requirements, control boards and other operational clearance must be modelled and associated with electrical equipment for collision checking. These clearance zones should be modelled as transparent solids or separate layers.

- [enter additional delivery team items here].

### 5.8.9 Fire protection services building information modelling

All other elements not mentioned below that the delivery team identifies as being required to complete deliverables for this stage must be agreed and a documented approach specified in this DBEP section below.

- Fire alarms and detection items modelled.

- Sprinklers and main sprinkler lines, and main branch lines modelled as generalised systems.

- Insulation around pipework shall be shown, with insulation thickness included on the modelled pipework. Insulation shall be separately indicated as a semi-transparent thickness around the pipework.

- Wall hydrants, fire department connections and risers modelled as generalised systems.

- Clearance zones for access, service space requirements, gauge reading, valve clearances and other operational clearances must be modelled and associated with the fire protection system and checked for conflicts with other elements. These clearance zones should be modelled as transparent solids or separate layers.

- [enter additional delivery team items here].

### 5.8.10 Quantity surveyor

All other elements not mentioned below that the delivery team identifies as being required to complete deliverables for this stage must be agreed and a documented approach specified in this DBEP section below.

A cost plan will be developed based on the following:

- The design intent BIM/s and dRofus created to date.

- The QS will take into consideration the model elements nominated above for each discipline.

- The QS will also use the model content plan to ensure each discipline has created its discipline-specific BIM based on the nominated objects.

- Any elements found by the QS, as per the below, must be remedied immediately by the relevant model element author:

  - not modelled as per above and model content plan

  - incorrectly modelled (floors as stairs)

  - incorrectly categorised (ceilings as slabs).

  - [enter additional delivery team items here].

### 5.8.11 [Other specialist disciplines/trades Building Information Modelling]

In addition to core design and engineering disciplines, healthcare projects frequently involve specialist trades and consultants that contribute critical systems to the overall design. Where engaged, these parties shall ensure their services are spatially and functionally coordinated within the BIM environment to support design integration, clash avoidance and informed decision-making. Typical disciplines may include (but are not limited to):

- Medical gases

- Nurse call

- Audio Visual

- Communications

- Security

- Pneumatic tube systems

- Wayfinding and signage

Where these services are in scope, the responsible appointed party shall document their BIM use for this project stage within this section. If no BIM deliverables are intended, this shall be explicitly stated. The delivery team BIM manager shall ensure all contributing disciplines are appropriately represented in the federated model and reflected in this BEP.

This section must be copied and renamed for each specialist.

- [Describe the BIM scope of work for this discipline, including which elements or systems will be represented in the model].

- [Specify file formats and model handover milestones for this discipline].

- [Describe how coordination with other disciplines will be managed].

    - 5.8.12 Detailed design information requirements deliverables

Refer to Section 6. for details of the information requirements due at detailed design.

    - 5.8 13 Detailed design building information modelling deliverables

The delivery team must produce BIM/s to a level that articulates the design intent and accurately represents the design solution by the end of detailed design, incorporating all of the elements in five, including:

- Updated DBEP in compliance with the PIR.

- Discipline-centric BIM/s in both native and IFC formats, incorporating all elements nominated in this section (if multiple models are being used, please share as transmittal package, e.g. eTransmit).

- Federated Model, built from IFC format trade/discipline BIM/s, delivered in the agreed format (as agreed per project).

- All IFC BIM/s to contain Queensland Health asset parameters specific to the stage, mapped to their respective QH_Information property sets.

- BIM/s and dRofus project database synchronised prior to extracts and delivery.

- Asset data extracted from BIM into the Queensland Health BIM Data Uploader Template.xlsx template and consolidated for all disciplines by the BIM manager.

- Project stage-specific BIM benefits realisation metrics shall be documented in Queensland Health BIM metrics for projects.xlsx template.

- Queensland Sustainability Spreadsheet.xlsx containing embodied carbon data for all applicable elements (concrete, steel, aluminium, glass), according to PIR Section 4.14.9.

    - 5.8.14 Building information modelling audit

An audit of all BIM files (including verifying consistency with dRofus) for the project will be undertaken by Queensland Health BIM advisor/s during detailed design (usually at 80% detailed design aligned with the design assurance submission). The advisor/s will assess the federated model to ensure alignment with the DBEP and PIR. The Queensland Health BIM data uploader template.xlsx shall be checked for compliant asset data, and both the Queensland Health BIM metrics for projects.xlsx and Queensland Health sustainability spreadsheet.xlsx shall be validated. A report with actions will be produced, and the delivery team will have a nominated time horizon to remedy any deficiencies. Any errors or omissions will need to be rectified by the originating authors and managed by the design BIM manager.

5.9 Tender documentation

PIR Section 3.8. All other elements not mentioned below that the delivery team identifies as being required to complete deliverables for this stage must be agreed and a documented approach specified in the DBEP section below.

### 5.9.1 Overview

The delivery team must produce discipline-centric BIM/s that define the design intent, allowing Queensland Health to tender the project to a selection of managing contractors.

This information shall be ready for construction modelling and be an accurate representation of the design. This level of detail includes sizes, finishes and materials for model components and should contain as few spatial coordination issues as possible.

Once BIM is complete for tender evaluation and award, it is ready to progress to workshop detailing and defined costing by tendering construction parties.

For tender documentation onwards, the BIM must contain the requirements of the previous project stages above and incorporate the following:

- Progressed BIM/s suitable for tender for all disciplines and documentation as specified for all project deliverables.

- Virtual coordination and clash detection as defined in section 6.8 of the DBEP and reported to the Queensland Health project management at nominated intervals.

- Asset parameters relevant to the tender shall be populated in the BIM/s as per section 4.14 of the PIR by each model element author as required.

- [enter additional delivery team items here].

### 5.9.2 Quantity surveyor

A cost plan will be developed based on the following:

- The design intent BIM/s and dRofus created to date.

- The QS will take into consideration the model elements for each discipline.

- The QS will also use the model content plan to ensure each discipline has created its discipline-specific BIM based on the nominated objects.

- [enter additional delivery team items here].

### 5.9.3 Tender documentation information requirements deliverables

Refer to section 6.4 for details of the information requirements due at tender documentation.

### 5.9.4 Tender evaluation and award building information modelling deliverables

For tender evaluation and award, the BIM/s must contain the requirements of all previous project stages above and incorporate the following:

- Each discipline BIM in native format and IFC, a 3D federated model based on IFC, a synchronised dRofus, the latest version of the DBEP, and original PIR and Queensland Health asset equipment lists for issue with tender documentation for contractor reference for main works packages (if multiple models are being used, please share as transmittal package, e.g. eTransmit).

- Design intent architectural and structural BIM/s are developed to represent the tender drawings. Services BIM/s will be modelled to depict systems and overall sizing of elements, ready for trade BIM/s to be produced.

BIM/s and dRofus project database synchronised prior to extracts and delivery.

- All IFC BIM/s to contain Queensland Health asset parameters specific to the stage, mapped to their respective QH_Information property sets.

- All design intent BIM/s shall achieve the requirements of the model content plan for tender evaluation and award.

- Asset data extracted from BIM into the Queensland Health BIM data uploader template.xlsx template and consolidated for all disciplines by the BIM manager.

### 5.9.5 Building information modelling audit

An audit of all BIM files (including dRofus) for the project will be undertaken by Queensland Health BIM advisor/s before tender documents are released to the market. The advisor/s will assess the federated model to ensure alignment with the DBEP and PIR. The Queensland Health BIM data uploader template.xlsx shall be checked for compliant asset data. A report with actions will be produced, and the delivery team will have a nominated time horizon to remedy any deficiencies. Any errors or omissions will need to be rectified by the originating authors and managed by the design BIM manager.

## 5.10 Construction documentation

PIR Section 3.9. All other elements not mentioned below that the delivery team identifies as being required to complete deliverables for this stage must be agreed and a documented approach specified in the DBEP section below.

### 5.10.1 Overview

The managing contractors shall use the design BIM/s and this DBEP to develop the approach for creating a CBEP and submit the CBEP as part of their tender.

The delivery team BIM/s will accurately represent the design solution by the end of construction documentation, incorporating all of the following elements:

- All discipline BIM/s are to be delivered to Queensland Health in the agreed open standard format (IFC 4 or later) containing all Queensland Health BIM shared parameters mapped to their respective Queensland Health Information property sets.

- All native BIM/s submitted are to be compatible and editable within the native BIM authoring tools. No BIM/s or objects shall be stripped of data, and all drawings and schedules should remain in and linked to the models.

- All construction documentation, including drawings and schedules, must be derived from the BIM environment and include information from dRofus.

- All BIM/s submitted to Queensland Health are to be ‘cleaned’ with all extraneous 2D references and 3D elements removed from the BIM/s. No BIM/s issued after construction documentation approval shall contain undefined, incorrectly defined or duplicated elements.

- All separately required deliverables related to the HHS computerised maintenance management system inputs for construction documentation requirements are to be achieved.

- Electronic drawing, BIM, and dRofus files are to be provided to Queensland Health on a hard drive or via Aconex, as applicable, unless otherwise agreed (e.g. by web file transfer or similar).

- Services are to be modelled to the ‘as designed’ size nominated by the consultant, including external and internal insulation, to enable coordination and confirmation of space requirements above ceilings and in risers.

- All duct and pipe services are modelled as closed systems to allow for system design parameters and system flow information to exist within the BIM/s.

- All equipment and associated terminating devices shall be assigned to a logical system and/or circuit/panel.

- Access and clearance zones shall be shown for each discipline, clearly labelled as such and included in the clash detection process. All BIM/s should consist of (if required) a separate 3D representation of plant egress and replacement routes.

- Asset parameters relevant to construction documentation shall be populated in the BIM/s, as per Section 4.14 of the PIR, by each model element author as required.

- [enter additional delivery team items here].

### 5.10.2 Civil building information modelling

All other elements not mentioned below that the delivery team identifies as being required to complete deliverables for this stage must be agreed and a documented approach specified in this DBEP section below.

[For construction documentation onwards, the BIM/s must contain the civil requirements of previous project stages above and any elements nominated below.]

- [enter additional appointed arty items here].

### 5.10.3 Landscape architect building information modelling

All other elements not mentioned below that the delivery team identifies as being required to complete deliverables for this stage must be agreed and a documented approach specified in this DBEP section below.

[For construction documentation onwards, the BIM must contain the landscape architecture requirements of previous project stages above and any elements nominated below.]

[enter additional delivery team items here].

### 5.10.4 Architectural building information modelling

All other elements not mentioned below that the delivery team identifies as being required to complete deliverables for this stage must be agreed and a documented approach specified in this DBEP section below.

For construction documentation onwards, the BIM/s must contain the architecture requirements of previous project stages above and any elements nominated below:

- Existing conditions.

- Demolished items.

- Rooms/spaces shall be defined as required for construction documentation, with the addition of BIM intelligence to support the creation of the room finish schedule and synchronised with dRofus. Floor and floor area usage will be measured and scheduled, requiring bound rooms to be created, named and numbered on their appropriate floor levels.

- Exterior walls, parapets and curtain walls shall be depicted to the designed height, length, width and ratings (thermal, acoustic, fire) to properly reflect the wall types. All walls shall be modelled with the necessary intelligence to produce accurate wall schedules.

- Architectural precast shall be modelled as individual discrete constructed elements, depicted to the designed height, length, width and ratings (thermal, acoustic, fire) to properly reflect precast element types. All precast elements shall be modelled with the necessary intelligence to produce accurate precast schedules.

- Exterior screens, sunshades and other architectural solar/rain control devices shall be depicted to the designed height, length, width and ratings (thermal, acoustic, fire) to properly reflect screen types. All screens shall be modelled with the necessary intelligence to produce accurate screening quantities.

- Roofs shall accurately represent the roof scape, slopes, drainage system, major penetrations and roof form (build-ups and materials). Intelligence shall include this and specification/build-up of the system, e.g. roof sheeting, insulation, battens, purlins, etc.

- Interior partitions shall be depicted to the designed height, length, width and ratings (thermal, acoustic, fire) to properly reflect wall types. Intelligence shall include this and specification/build-up of the system, e.g. 70mm stud, 2x1mm plasterboard each face, etc. All finishes need to be included within the wall type, regardless of the thickness of the finish.

- Doors, windows and louvres are depicted to represent their designed size, type and location. All doors and windows shall be modelled with the necessary intelligence to produce accurate window and door schedules from the BIM or dRofus (i.e. intelligence contains reference number, location, structural opening, wall thickness, door-set overall size, leaf sizes, vision panel/configuration. Detail items such as fire rating, acoustic rating, frame and door materials and finishes, swing type and hand, and ironmongery sets must be documented in the schedule.

- All budget group one, two and three FF+E and other architectural FF+E shall be accurately depicted. Intelligence shall contain AusHFG code, manufacturer, range/series name, model reference number, size and engineering services information, where known. For tier one and two projects, refer to the dRofus management plan for a detailed list of FFE items required to be modelled.

- Specialist joinery shall be accurately depicted. Where furniture or furniture systems are added to the architectural model for purely visualisation purposes, these model components should be created in the model category of entourage and not furniture.

- Ceilings and soffits shall be depicted at the correct heights, dimensions, and with the correct materials. Ceilings shall be set at the correct height, and the depth of the ceiling shall reflect the construction build-up. Ceiling grids shall be located in the model.

- Insulation above ceilings and insulation fixed to wall faces, and slab soffits (e.g. plant rooms) shall be shown, with insulation thickness indicated as a semi-transparent thickness/layer.

- The architectural BIM/s shall be fully coordinated with the structural BIM/s, including concrete profiles, thickness, penetrations and primary and secondary steel (such as supporting members within partitions).

- Stairs and ramps shall be accurately depicted with all components (i.e. architectural treads and risers, handrails, guardrails, nosings, etc.). Concrete stairs and associated components, floor slabs shall be developed in the structural BIM/s and then referenced by the architectural model for each floor of the building. Intelligence shall contain manufacturer, range/series name, model reference number, size as well as height, length, width, materials.

- Model mechanical, electrical and hydraulic items that require architectural connectors (toilets/sinks/etc.), require colour/finish selection (louvres, diffusers, etc.) that affect 3D visualisation (lighting fixtures) unless provided by engineers.

- ‘No-go’ zones for structure and services over equipment must be modelled and checked for conflicts with other elements, e.g. secondary steel over operable walls and access for installing and removing ceiling-mounted pendant equipment.

- Schedules: extract accurate door, window, hardware schedules and ceiling, wall and floor finish schedules indicating the type, materials and finishes used in the construction. These schedules must be extracted from the BIM/s or dRofus— intelligence must be synchronised with the model/s.

- [enter additional delivery team items here].

### 5.10.5 Structural building information modelling

All other elements not mentioned below that the delivery team identifies as being required to complete deliverables for this stage must be agreed and a documented approach specified in this DBEP section below.

- For construction documentation onwards, the BIM/s must contain the structural engineering requirements of previous project stages above and any elements nominated below:

- All foundations, including piles, pads, footing elements and rock anchors. Intelligence includes height, width, depth, top of footing and concrete grade.

- Structural floor slabs shall be accurately depicted, including all necessary recesses, curbs, pads, closure pours, expansion joints, pour joints and penetrations 150mm diameter or larger and concrete grade. Steel reinforcing in concrete and embedded in concrete may be modelled at the delivery team's discretion.

- Concrete columns shall be accurately depicted, including all necessary recesses and penetrations, and concrete grade. Steel reinforcing in concrete and embedded in concrete may be modelled at the delivery team's discretion.

- All steel columns, primary and secondary framing members and bracing for the roof (including decks), shall be depicted to the designed shape, height, length and width, including all necessary intelligence to produce accurate structural steel framing plans and related building/wall sections.

- Load bearing and other structural wall types including openings shall be depicted to the designed height, length, width and ratings (e.g. fire, if not provided in the architect’s model) and all necessary intelligence to produce accurate structural wall framing plans and related building/wall sections.

- Structural precast elements modelled as individual discrete constructed elements depicted to the designed height, length, width and ratings (fire) to properly reflect precast element types. All precast elements shall be modelled with the necessary intelligence to produce accurate precast schedules. Hollow core planks may be modelled as a slab unless coordination with mechanical systems needs to occur due to the hollow core being used for those systems.

- All concrete stairs (not modelled by the architect), landings, necessary openings and steel stair framing members for stair systems shall be depicted to the designed height, length, width and ratings (e.g. fire, if not provided by the architect).

- All necessary shafts, pits, sumps and openings, including necessary intelligence to produce accurate plans and building/wall sections depicting these design elements.

- The BIM/s shall include necessary intelligence to reflect accurate quantities by type and finishes.

- [enter additional delivery team items here].

### 5.10.6 Mechanical building information modelling

All other elements not mentioned below that the delivery team identifies as being required to complete deliverables for this stage must be agreed and a documented approach specified in this DBEP section below.

For construction documentation, the BIM/s must contain the mechanical requirements of previous project stages above and any elements nominated below:

- Services are modelled to the designed size nominated by the consultant, including external insulation, to enable coordination and confirmation of space requirements above ceilings and in risers.

- All duct and pipe services are modelled as closed systems (with insulation) to allow for system design parameters and system flow information to exist within the BIM/s.

- All equipment and associated terminating devices shall be assigned to a logical system.

- All BIM/s include separate 3D representations of required access and clearances for all services equipment inspection, repair, maintenance and replacement, light fixture access, ‘shutdown’ valve access, overhead cable tray access, etc. Access and clearance objects should be separate for each discipline, clearly labelled as such, and included in the clash detection process.

- [enter additional delivery team items here].

### 5.10.7 Hydraulic building information modelling

All other elements not mentioned below that the delivery team identifies as being required to complete deliverables for this stage must be agreed and a documented approach specified in this DBEP section below.

For construction documentation, the BIM/s must contain the hydraulic requirements of previous project stages above and any elements nominated below:

- Stormwater, waste and vent, water supply, rainwater collection, trade waste, etc.

- Piping modelled to room extents as defined systems and/or to the fixture as agreed in the BEP/model content plan.

- Lagging/insulation around pipework shall be shown, with insulation thickness included on the modelled pipework. Insulation shall be separately indicated as a semi-transparent thickness around the pipework.

- Roof and floor drains, leaders, sumps, grease arrestors, tanks, water treatments and other major items.

- Booster pumps.

- Modelling of fixtures to be agreed with the architect and documented in the BEP/model content plan (e.g. sinks, basins, toilet and bathroom fixtures, cisterns and water tanks).

- Clearance zones for access, service space requirements, gauge reading, valve clearances and other maintenance and operational clearance must be modelled and associated with the hydraulic system and checked for conflicts with other elements.

- The BIM/s shall include necessary intelligence to create specific systems providing all the schedules typically required for the discipline in an accurate and complete manner.

- [enter additional delivery team items here].

### 5.10.8 Electrical building information modelling

All other elements not mentioned below that the delivery team identifies as being required to complete deliverables for this stage must be agreed and a documented approach specified in this DBEP section below.

For construction documentation, the BIM/s must contain the electrical requirements of previous project stages above and any elements nominated below:

- Permanently mounted lighting fixtures (moveable socket outlets need not be modelled as part of the electrical package unless needed for socket load calculations or for estimating purposes within a loose furnishing package).

- Light fixture components shall include lamp type and photometric information, including light loss factor, initial intensity and initial colour temperature.

- Fire alarms and security systems.

- Input devices and notification devices.

- Associated equipment and access clearances.

- Building controls.

- All cable trays (including fire rating as appropriate).

- Clearance zones for access, service space requirements, gauge reading, and other operational clearance must be modelled and associated with the electrical equipment for collision checking.

- The BIM/s shall include necessary intelligence to provide/extract all the schedules typically required for the discipline accurately and completely; and all other elements not mentioned above, as required, as specific systems.

- [enter additional delivery team items here].

### 5.10.9 Fire protection services building information modelling

All other elements not mentioned below that the delivery team identifies as being required to complete deliverables for this stage must be agreed and a documented approach specified in this DBEP section below.

For construction documentation, the BIM/s must contain the fire protection services requirements of previous project stages above and any elements nominated below:

- Sprinkler lines from a diameter of 25mm and over.

- Sprinkler heads.

- Fire protection pumps.

- Standpipes, wall hydrants, fire department connections, risers, including valve clearances.

- Insulation around pipework shall be shown, with insulation thickness included on the modelled pipework. Insulation shall be separately indicated as a semi-transparent thickness around the pipework.

- Fire alarm/mass notification devices and detection systems.

- Clearance zones for access, service space requirements, gauge reading, valve clearances and other operational clearances must be modelled and associated with the fire protections system and checked for conflicts with other elements.

- The BIM/s shall include necessary intelligence to provide/extract all the schedules typically required for the discipline in an accurate and complete manner and all other elements not mentioned above, as required as specific systems.

- [enter additional delivery team items here].

### 5.10.10 Quantity surveyor

All other elements not mentioned below that the delivery team identifies as being required to complete deliverables for this stage must be agreed and a documented approach specified in this DBEP section below.

A cost plan will be developed based on the following:

- The design intent BIM/s and project database created to date.

- The QS will take into consideration the elements nominated above for each discipline.

- The QS will also use the model content plan to ensure each discipline has created their discipline-specific BIM based on the nominated objects.

- Any elements found by the QS, as per the below, must be remedied immediately by the relevant model author:

  - not modelled as per above and model content plan

  - incorrectly modelled (floors as stairs)

  - incorrectly categorised (ceilings as slabs).

  - [enter additional delivery team items here].

### 5.10.11 Other specialist disciplines/trades building information modelling

In addition to core design and engineering disciplines, healthcare projects frequently involve specialist trades and consultants that contribute critical systems to the overall design. Where engaged, these parties shall ensure their services are spatially and functionally coordinated within the BIM environment to support design integration, clash avoidance and informed decision-making. Typical disciplines may include (but are not limited to):

- medical gases

- nurse call

- audio visual

- communications

- security

- pneumatic tube systems

- wayfinding and signage.

Where these services are in scope, the responsible appointed party shall document their BIM use for this project stage within this section. If no BIM deliverables are intended, this shall be explicitly stated. The delivery team BIM manager shall ensure all contributing disciplines are appropriately represented in the federated model and reflected in this BEP.

This section must be copied and renamed for each specialist.

- [Describe the BIM scope of work for this discipline, including which elements or systems will be represented in the model].

- [Specify file formats and model handover milestones for this discipline].

- [Describe how coordination with other disciplines will be managed].

### 5.10.12 Construction documentation information requirements deliverables

Refer to Section 6.4 for details of the information requirements due at construction documentation.

5.10.13 Construction documentation building information modelling deliverables

The delivery team must produce BIM/s to a level that articulates the design intent and accurately represents the design solution by the end of construction documentation, incorporating all of the following elements:

- Updated DBEP in compliance with the PIR.

- Discipline-centric BIM/s in both native and IFC formats, incorporating all model elements nominated in this section (if multiple models are being used, please share as transmittal package, e.g. eTransmit).

- Federated model, built from IFC format trade/discipline BIM/s, delivered in the agreed format (as agreed per project).

- BIM/s and dRofus project database synchronised prior to extracts and delivery.

- IFC BIM/s to contain all Queensland Health BIM shared parameters mapped to their respective QH_Information Property Sets (as per Queensland Health IFC export mapping).

- Asset data extracted from BIM into the Queensland Health BIM data uploader template.xlsx template and consolidated for all disciplines into a single file by the BIM manager.

### 5.10.14 Building information modelling audit

An audit of all BIM/s (including dRofus) for the project will be undertaken by Queensland Health BIM advisor/s during construction documentation. The advisor/s will assess the federated model to ensure alignment with the DBEP and PIR. The Queensland Health BIM data uploader template.xlsx shall be checked for compliant asset data. A report with actions will be produced, and the delivery team will have a nominated time horizon to remedy any deficiencies. Any errors or omissions will need to be rectified by the originating authors and managed by the design BIM manager.

5.11 Construction

See CBEP documentation.

6 Technical

The following section reflects the expected uses for BIM on the project, aligned to the PIR. Changing uses of BIM during the project changes the scope of service previously agreed/documented and has contractual implications. To reduce the risk of disputes, manage changes in conformance with the terms and conditions in agreements and contracts and keep a cumulative record of agreed changes in a constant location, e.g. the BEP. Each version of the BEP should highlight changes approved since the issue of the previous version.

6.1 Software selection

PIR Section 2.3, 4.7, 4.9 - 4.11. Add other delivery team members and software as necessary.

The delivery team's chosen (buildingSMART IFC certified) BIM authoring tools are recorded in table 10. Once endorsed by the delivery team, use of different versions is not permitted without approval from the nominated Queensland Health representative.

| Disciplines | Software (version/build) | Use |
| --- | --- | --- |
| Cost planning | [enter] | Costing |
| Architecture | [enter] | Design authoring |
| Structure | [enter] | Design authoring |
| Hydraulic | [enter] | Design authoring |
| Mechanical | [enter] | Design authoring |
| Electrical | [enter] | Design authoring |
| Fire | [enter] | Design authoring |
| Civil | [enter] | Design authoring |
| Wayfinding | [enter] | Design authoring |
| Communications | [enter] | Design authoring |
| Security | [enter] | Design authoring |
| Audio visual | [enter] | Design authoring |
| Nurse call | [enter] | Design authoring |
| Medical gases | [enter] | Design authoring |
| Pneumatic | [enter] | Design authoring |
| Delivery team collaboration | [enter] | Model collaboration |
| Delivery team collaboration | [enter] | Document management system |
| Delivery team coordination | [enter] | Clash detection/avoidance |
| Delivery team coordination | [enter] | Issue tracking |

Table 10: Software selection

6.2 Project common data environment

PIR 2, 4.12 nominates the project CDE for design and how access will be managed for Queensland Health representatives.

[enter CDE details here or refer to relevant documents]

### 6.2.1 Information status, revision and classification

Document the proposed approach to managing the information containers held within the CDE, including status (concept, SD, DD, CD), revision (1, 2, 3, and A, B, C, etc.), and information container classification. Check the Aconex guide if relevant

[enter details here]

### 6.2.2 Information containers

PIR section 4.4. Appointed parties to document the information containers graphically showing the relationships, e.g. cost plan, discipline BIM/s versus. Trade models and federated model, interaction with the CDE, etc. Check the Aconex guide if relevant

The diagram below identifies the high-level information delivery plan and the associated information containers.

[enter diagram here]

### 6.2.3 Collaboration resources

Detail how to request access, uses of each system/platform, etc. below.

The details of the project’s collaboration resources are documented below.

[enter details here]

### 6.2.4 Exchange frequency

Use this section to define a table showing model element authors, model formats (native, IFC, etc), frequency of exchange (e.g. weekly, milestone, etc.)

[enter details here]

| Disciplines | Weekly collaboration (native formats) | Fortnightly HIQ submission (IFC format) | Project stage milestones (native and IFC formats) |
| --- | --- | --- | --- |
| Federated model | [enter – e.g. upload to cloud model collaboration tool, Issue tracking, etc.] | [enter – e.g. upload to cloud model collaboration tool, etc.] | [enter – e.g. upload to cloud model collaboration tool, Issue tracking, Aconex, etc.] |
| Cost planning | [enter] | [enter] | [enter] |
| Architecture | [enter] | [enter] | [enter] |
| Structure | [enter] | [enter] | [enter] |
| Hydraulic | [enter] | [enter] | [enter] |
| Mechanical | [enter] | [enter] | [enter] |
| Electrical | [enter] | [enter] | [enter] |
| Fire | [enter] | [enter] | [enter] |
| Civil | [enter] | [enter] | [enter] |
| [enter] | [enter] | [enter] | [enter] |

Table 11: Model exchange frequency

6.3 Industry foundation classes

PIR Section 4.11 describes the IFC requirements for the project.

### 6.3.1 Export settings: Revit to information foundation classes

The steps below outline the process to deliver an IFC format BIM from Autodesk Revit. Other authoring tools should follow the same principles regarding mapping Queensland Health BIM shared parameters to QH_Information IFC property sets as defined in Section 6.4.1

Figure 1: Step 1 – Exporting IFC from Revit

In the relevant 3D export view in Revit (refer to figure 1: step 1 – exporting IFC from Revit):

- Select File.

- Select Export.

- Select IFC.

- Select Modify setup.

Figure 2: step 2 – Exporting IFC from Revit

In the ‘modify setup’ dialogue box (refer to figure 2):

- Select the Property sets tab, ensure relevant tick boxes are checked.

- Browse to and select the Queensland Health IFC export mapping file.

- Click Ok and export as usual.

Other settings may be adjusted as required, but the result shall be all Queensland Health BIM shared parameters being successfully mapped to the relevant QH_Information property set tab in IFC (refer to Figure 3).

Figure 3 Example IFC showing QH_Information Property Set tab

6.4 Information requirements

Queensland Health recognises that during delivery, it may not be practical for project teams to store data in model environments. As such, it is up to the delivery team to determine and document in the BEP how they intend to distribute, collate and verify required asset data.

This section focuses on the alphanumerical (non-geometric) component of the ‘Level of information need’, specifically the structured data that must be attributed to modelled elements within the BIM/s.

The PIR outlines the authoritative source of Queensland Health’s information requirements, including asset groupings, classification, functional location numbering, room codes and attribution at each project stage.

The delivery team shall refer directly to the PIR to determine the specific attributes and classifications applicable to each element or asset group. Also see the Queensland Health asset equipment lists for greater detail and the BIM data uploader for source lists.

[enter here].

### 6.4.1 Attributes

Queensland Health has prefixed all parameter names with QH_ as they relate directly to Queensland Health's needs. These parameters are available preconfigured for the project environment in Autodesk Revit 2024. It is understood that not all designers use this BIM authoring tool, and it is hoped that future versions may provide preconfigured parameters for other applications if requested.

Schedules for each asset group have been provided in the Queensland Health Project Schedules (Revit)_2024.rvt file and should be copied into each model using the instructions contained in the file.

All shared parameters provided in the Queensland Health Shared Parameter and Queensland Health dRofus Shared Parameter file must be used to create shared parameters in Autodesk Revit. The Global Unique Identifier (GUID) of the project shared parameter shall match the GUID in the Queensland Health provided TXT files.

Figure 4: Adding parameters and exporting asset schedules

If these documents aren’t compatible with selected BIM authoring tools, use the attributes by grouping tab in the Queensland Health asset equipment lists spreadsheet to configure the parameters.

### 6.4.2 Hospital and health service building, floor/level and zoning naming

[enter here].

6.5 Documentation

PIR Section 4.1 (m). Appointed parties shall use HHS coding. Engage with the relevant Queensland Health representative to obtain the necessary details, such as functional location code values, level naming, etc., at the beginning of the project.

The following 2D documentation is not derived from BIM.

| Discipline | Documentation type | Comments |
| --- | --- | --- |
| Structure | Typical reo details | Typical reinforcement details are documented in CAD |
| Architecture | Railing details | 1:5 Railing details |
| - | Specifications | [enter] |

Table 13: 2D documentation external to BIM

## 6.6 Schedules

PIR Section 2 and 2 (c). Appointed parties are to generate all schedules as extractions from the discipline/trade BIM/s and/or space planning tool. Any schedule not produced by these means must be documented here. The approach for coordinating these detached schedules with other information containers (BIM, dRofus, etc.) must be documented and approved by the Queensland Health representative prior to undertaking this work.

[list schedules not from BIM and detail the approach to coordinating these schedules with BIM here]

6.7 Room data sheets

PIR Section 3.5 and 3.7. Appointed parties must nominate the approach for producing RDS for the project, as one element of the overall PIM.

[enter approach to generating and coordinating RDS contents here]

6.8 Federated model and coordination

PIR Section 4.6. The delivery team is to document the approach to managing hard clashes, construction tolerances, safe working/maintenance zones, responsibilities and accountabilities, clash detection priorities, tolerance strategy, and outputs (e.g., coordination reports, dashboarding, etc.).

### 6.8.1 General

The delivery team are to use automated conflict checking/clash detection software during schematic design onwards to determine geometric clashes in each discipline/trade BIM and then in the federated model. Once issues are identified, each discipline/trade shall resolve the model elements within the BIM/s they are responsible for.

The identification and reporting of coordination issues should be held regularly (e.g. weekly or fortnightly) during the last half of schematic design and throughout detailed design and construction documentation. These reports should show any outstanding coordination issues between the delivery team members.

Queensland Health expects the coordination to be appropriate to the stage of the project (e.g. reducing coordination issues as the project progresses). Major space planning coordination issues between architecture, structure, mechanical and other relevant services should be resolved by the end of detailed design. Construction coordination should be largely resolved by the end of construction documentation. All design projects should be fully coordinated and constructable.

### 6.8.2 Tolerances

The delivery team must set minimum tolerances for clash detection for project stage deliverables. These tolerances may vary between stages, for example, moving from a 100mm tolerance at schematic design to a 25mm tolerance during construction documentation.

[enter tolerances here].

### 6.8.3 Clash tests

[All information required to undertake clash tests must be documented in the DBEP]

Consider which stage of the project various clash tests are most appropriate for, e.g. focusing on architectural vs structural earlier, before introducing services. All information required to undertake clash tests must be documented below.

[enter clash test strategy here].

### 6.8.4 All other clashes

While the above clashes have been assigned priorities, other clashes will exist within the BIM/s. These other clashes should not be ignored, nor should they be discarded. The intention is to have a federated model that has minimal coordination issues prior to completion of each project stage. There must be documented proof that the delivery team has addressed the coordination issues, where identified.

### 6.8.5 Coordination responsibilities

- The delivery team BIM manager facilitates the overall coordination and management of clashes during the design stages.

- The services consultants are responsible for discovering, managing and resolving clashes between services disciplines prior to the issue of discipline BIM/s to the BIM manager for clash detection.

### 6.8.6 Clash resolution meetings during design stages

Consider what outcomes are expected from clash meetings are designers attending to resolve issues, or are BIM coordinators attending to prioritise identified issues in the issue tracking software, etc? What is the approach to hosting productive clash meetings?

[enter the approach for clash resolution meetings here].

### 6.8.7 Clash detection meetings during construction stage

The contractor is responsible for arranging similar clash detection meetings during the construction stages (see CBEP).

6.9 Quality assurance and control

PIR Section 4.8. Quality assurance/control procedures, retaining data integrity/accuracy in BIM and integration approach with cost planning, construction staging/sequencing, SoA, space planning and resulting 2D drawing and schedule outputs.

The below outlines the model and data quality control approaches, including responsible parties and frequency/timeframes.

[enter response/table here].

# 7 Appendices

7.1 Appendix A – Building information modelling manager

This appendix is required only for pre-contract evaluation and must be removed post-tender.

### 7.1.1 Building information modelling manager experience

The BIM manager appointed by the delivery team and named in Table 7 has the following experience.

#### 7.1.1.1 Experience

PIR Section 4.2. State the experience of the named individual (or individuals) performing BIM management roles, including: number of years, projects delivered, technical competencies and communication abilities

#### 7.1.1.2 Resource allocation

State the estimated time of the named individual (or individuals) performing BIM management roles for the project.

| Stage | Named resource | BIM and information management tasks | Time allocation per week |
| --- | --- | --- | --- |

Table 14: BIM management

7.2 Appendix B – Quantity surveyor requirements or model content plan

Refer to ‘Australian Institute of Quantity Surveyors’ guidance material.